## Calculator
HYBRID INVERTER + LITHIUM BATTERY CALCULATOR
STEP 1 — PROJECT INPUTS
Maximum simultaneous load | 5 | kW | All important loads that may run together
Desired backup load | 3 | kW | Load you actually want to run during power cut
Backup duration | 6 | hours | Required battery backup
LiFePO4 DoD | 90 | % | Use actual battery manufacturer's allowed DoD
Battery/system efficiency | 92 | % | Use actual inverter+battery data where available
Design reserve | 10 | % | Extra design margin
Battery unit capacity | 5.12 | kWh | Example: 51.2V × 100Ah
Battery nominal voltage | 51.2 | V | Example LV LiFePO4
Battery unit capacity | 100 | Ah | Example 51.2V 100Ah
STEP 2 — AUTOMATIC RESULTS
Backup energy required |  | kWh | Backup load × hours
Required battery bank |  | kWh | Energy adjusted for DoD, efficiency & reserve
Battery units required |  | units | Always round UP
Installed battery capacity |  | kWh | Battery units × unit capacity
Installed battery Ah |  | Ah | At nominal battery voltage
Approx. continuous battery current |  | A | Approx.; verify actual inverter/BMS limits
Suggested inverter minimum |  | kW | Planning estimate with 25% headroom
Recommended inverter class |  |  | Final model must be checked against actual load & surge
IMPORTANT: This is a planning calculator, not a final engineering design. For actual installation, verify inverter surge rating, continuous output, battery charge/discharge current, BMS limits, battery temperature/derating, cable/protection, phase balance, and manufacturer compatibility.

## Load List
OPTIONAL — BUILD THE LOAD FROM APPLIANCES
Appliance | Watts | Qty | Running kW | Backup? (1=Yes) | Backup kW | Backup hours | Backup kWh
Lights | 20 | 10 |  | 1 |  | 6
Fans | 70 | 4 |  | 1 |  | 6
Fridge | 200 | 1 |  | 1 |  | 8
TV | 120 | 1 |  | 1 |  | 4
Router | 20 | 1 |  | 1 |  | 12
AC | 1200 | 1 |  | 0 |  | 6
Pump | 750 | 1 |  | 0 |  | 1
Other | 0 | 1 |  | 0 |  | 1
TOTAL
Tip: | Take the maximum simultaneous running load for inverter sizing and the selected backup load for battery sizing.

## How It Works
HOW THE CALCULATOR WORKS
1 | Enter maximum simultaneous load (kW).
2 | Enter desired backup load (kW).
3 | Enter backup hours.
4 | Enter actual LiFePO4 DoD, efficiency and battery unit kWh.
5 | Battery energy = backup kW × hours.
6 | Required battery bank = energy ÷ (DoD × efficiency) × (1 + reserve).
7 | Battery count = required battery kWh ÷ battery-unit kWh, rounded UP.
8 | Inverter planning size = max simultaneous load × headroom. Then verify surge/current/model specifications.
IMPORTANT | Electricity bill alone cannot determine inverter kW. Use bill for energy consumption; use connected/simultaneous load and maximum demand for inverter sizing.